SHFD4 Meeting Notes February 17, 2026

Present: Jim Robistow, Rick Whittlesey, Devin Hackett, Ken Little, Kevin Winch (via Telephone) Cindy Spence

Jim called the meeting to order at 7PM

Rick made a motion to waive the reading aloud of the minutes. Jim seconded. All in favor. Motion passed.

Treasurer’s Report

| Checking Account | $221,539.29 |
| --- | --- |
| Money Market | $135,348.72 |
| Accounts Receivable | $38,369.81 |
| Payment Received | $630.00 |
| Total | $395,887.82 |

- The accounting fee went from $1500 to $2500 with no warning. THis needs to be negotiated with NIcole. We expected to pay more for sending letters out but did not expect the new monthly bill. Rick and Kevin will handle the negotiation.

- Bills from Green Mountain have not come in and have not been paid.

- Jim made a motion to accept the financials. Kevin seconded and all were in favor. Motion passed.

- Draft budget is good to go and will be adjusted as necessary. Old Business:

- Kevin sent a letter to Buerman’s Engineering concerning 5 units for Nate Hayward. JIm is going through the invoices to see what is actually billed. We think it is 5 suspensions and 1 full rate. Nate and Jay want to come to the March meeting to discuss. Kevin will respond to them.

- We will not be responsible for leaks for the town park if the fountain freezes- it’s on the town

Operator’s Report

- The monthly operations report was completed and submitted.

- The monthly WR-43 was completed and submitted.

- The monthly coliform sample was taken.

- The first quarter samples were taken.

- Someone reported a leak in front of Pans Pizza. An old galvanized line was found that nobody knows where it goes or where it comes from. It was repaired and then leaked again a few days later because the repair clamp was not correct for the pipe. This line will have to be replaced at some point.

- The leaking check valve was replaced on filter 1. It all looked good and then we found another leak on the threaded T in an untouched area of piping. We disassembled that section and put thread sealant on the T.  All filters are back in operation.

- The influent flows to the filters were adjusted. There are periodic filter alarms that are caused by high pressure coming into the filter. I believe these are caused by excessive flow into the filters causing a pressure spike on the inlet side.

- An adjustment in chlorine mixture was done to try and get a better consistent residual. We are still playing around with it. The biggest issue is every time the day tank is filled, a substantial increase in chlorine residual occurs.

- Watson Marlow was contacted to see if there is a different pump head that can be used on the chlorine pump.  There is not.

- We noticed the filters are forming mud balls. This is causing shorter filter runs. A reduction was made to the polymer and the air scour time was increased on the backwashes. This should break up the mud balls, but it will take some time.

- Filter 2 has some water entering the filter during the air scour so we are not able to increase the air scour time that much. We are looking into the cause of that. It might be  a programming issue that we can contact Mark Mallett to fix.

- Routine maintenance was done on the chlorine analyzer.

- The 2am flows have dropped significantly since some leaks have been fixed.

Upcoming Projects

Replace the chemical feed tubing Mud ball removal in filters Cleaning of clear well 1

DBP sample in February

1 PFAS sample in February

1 PFAS sample April 1 – June 30

- Kevin W will change the exhaust motor when he gets back

- Ask Kevin Knapp to attend the April 14 meeting. Ongoing Business

- Jim has taken on looking at all the 911 addresses and comparing them to the invoices to make sure it all adds up. He could use some help. Rick volunteered to look at Allen Pt and South St, Hochelage road, Turtle Bay, Whipple Rd and West Shore Road.

- Cindy reports one property sold- KB020 from Shirlock to Ashley Group.

- Liens file- Rick made a motion to file liens against Hop Haulers and Timothy Bryan. Jim seconded and all were in favor. CIndy will bring it to the town office.

- Phone system- Jim has been in contact but nothing has been resolved. Tabled for now.

- Table redundant piping

- Lead/Copper - the state is paying MSK for Phase 1 identification. They will supply test kits . Phase II $355,000  Phase III $58,000

- Ask Patrick Smart to meet at some point with Jim and Rick.

- Keelers Bay Associates- Jim counts 9.5 units. One more building lot than what we said. They are paying for 8.5. Send letters to all who bought from Gammal to formalize what they are paying for. Devin will brainstorm a letter for that.

Kevin made a motion to adjourn. Devin seconded. All were in favor. Meeting adjourned at 8:23